Email from Phil Jalbert, EPA regarding radon at Zephyr Cove Elementary School

March 6, 2008

Ms. Teri Jamin, President 
Douglas County School Board 
1638 Mono Avenue 
P.O. Box 1888 
Minden, Nevada   89423

Dear Ms. Jamin:

Thank  you  for  your  letter  of  February  19,  2008  requesting 
assistance  in answering questions posed by you and Ms. Luna with regard 
to   the  Zephyr  Cove  Elementary  School  (ZCES).   We  also  received 
additional information from Mr. Greg Felton.  He provided the minutes of 
the School Board Meeting (February 12, 2008) and a detailed email (March 
4,  2008)  on his observations and five questions related to radon risk. 
We  normally  refer  such requests to our Regional offices.  However, in 
this  case,  the  EPA  Region  9  office (San Francisco) has asked us to 
respond directly to your request.

Please   be  aware  that  this  response  is  based  only  on  the 
information  we  have  received.   Therefore, in the absence of complete 
information  or a site inspection, we’ve limited our response to several 
general   observations  and  recommendations.   Our  response  addresses 
measurement,  risk, mitigation and technical assistance.  EPA’s policies 
on  radon  measurement  and  mitigation are necessarily conservative and 
protective, and based on many years of research and experience in a wide 
variety  of  buildings, including schools.  EPA’s guidance on radon is a 
prudent  and cost-effective long-term approach to risk reduction that is 
protective of students and staff alike.

Radon  measurement.   EPA’s  recommended  action  level  has always been 
primarily  defined  as  a  radon gas measurement, i.e., 4 picocuries per 
liter  of  air  (pCi/L).   The Fallon report incorrectly claims that EPA 
views  working  level (WL or progeny) measurements as equally acceptable 
to radon gas (pCi/L) measurements.  Radon gas measurements should always 
be  preferred,  especially  when  the measurement result will be used in 
mitigation decisions.

Since  the  actual  radon  gas  measurements  from  the  ZCES  are 
available,  they  should  be  used in mitigation decisions, provided the 
measurements  were obtained in accordance with the EPA Radon Measurement 
in  Schools Protocol (EPA 420-R-92-014, July 1993). The Schools protocol 
allows  for  initial  short-term  measurements  to be conducted in every 
ground  contact  room.   Measurement  results at or above 4 pCi/L (e.g., 
4-10  pCi/L) should be verified with follow-up measurements which can be 
long-term  or short-term.  Long-term measurements (90-days+) give a more 
accurate estimate of the average annual radon level.

Making  a  good  working  level  or  progeny  measurement  is more 
difficult   than  making  a  radon  gas  measurement.   Because  of  the 
uncertainties  associated  with  progeny  measurements, the state of New 
Jersey   and   the   American   Association   of  Radon  Scientists  and 
Technologists (AARST) do not recommend making mitigation decisions based 
on  working  level  measurements.   Working  level (WL) measurements are 
mentioned  very  briefly  in  EPA  documents.  The main reason for their 
inclusion  is  that in the early years of EPA’s radon program there were 
some  devices  being  used  in  the  market  to  measure  working  level 
(progeny).   The  use  of  WL  devices has declined over time due to the 
difficulty and expense of making such measurements.

For   the  reasons  above,  EPA’s  recommendation  is  to  base  a 
mitigation   decision   on  a  gas  measurement,  which  we  consider  a 
conservative  and  protective,  as  well  as  practical  way to evaluate 
potential  risk.   More simply put, “no radon gas, no risk.”  Of course, 
there  is rarely, if ever, “no” radon gas.  Background concentrations of 
radon  in outdoor air can vary from place to place and time of day.  The 
available  data  suggest that the outdoor average is about 0.4 pCi/L, or 
1/10th EPA’s action level.

Radon  health  risk.   To  our knowledge, lung cancer is the only health 
effect from exposure to radon in air.  There are no data to suggest that 
children  are  at  greater  risk  from exposure to radon in air than are 
adults.   Recent  radon  risk  assessments  confirm  that  the  risk  at 
relatively  low  levels  of  radon is significant.  For this reason, EPA 
recommends that mitigation be considered at levels even below our action 
level  of  4  pCi/L  (and  specifically  between  2  and  4  pCi/L)  for 
residential  structures.   As you know, the 2003 EPA risk assessment 
estimated   20,000   annual  radon-related  lung  cancer  deaths.   It’s 
important  to  remember  that this estimate is based on exposure to 1.25 
pCi/L,  which  is  the average U.S. indoor radon level.  It is for these 
reasons that the International Commission on Radiation Protection (ICRP) 
recommends  that  radon  be  reduced  to  a  level  as low as reasonably 
achievable (ALARA).

Mitigation.   EPA’s principal recommendation for mitigating radon levels 
in  school  buildings  is  to  control  the source, i.e., to minimize or 
prevent  radon entry.  The technique used most often and successfully is 
sub-slab  or  sub-membrane Active Soil Depressurization (ASD).  From the 
Fallon report we reviewed, it appears that the existing ZCES ASD systems 
have not been adequately evaluated for their effectiveness.

A  complete  and  thorough  evaluation of the existing ASD systems 
should be conducted.  The evaluation should identify needed upgrades to, 
or  extensions  of, the existing radon mitigation systems.  Any upgrades 
or  new  systems  should  conform  to EPA’s guidance.  We recommend that 
school ASD systems be operated continuously.

For the school’s slab-on-grade footprint not served by an existing 
ASD  system,  if  measurement  results  warrant  mitigation,  additional 
diagnostics  should  be  done  to determine whether ASD can be employed. 
These   evaluation/diagnostic   activities  should  be  conducted  by  a 
qualified    professional    with   experience   in   large,   low-rise, 
slab-on-grade/crawlspace  school/commercial  buildings.  Evaluations and 
diagnostics  can be conducted independent of weather conditions and when 
convenient.

EPA  does not recommend filtration as a radon control measure; the 
use  of  High  Efficiency  Particle Air (HEPA) filtration devices is not 
recommended  as  a  mitigation  technique.  While there is evidence that 
filtration  can  reduce progeny concentrations, many factors can impinge 
on  the  effectiveness  of  filtration  in  maintaining  reduced progeny 
concentrations with an attendant reduction in radon dose.

Some  of  these complicating factors include: a potential increase 
in  ultra fine particles available for progeny attachment and deposition 
in the lung; a potentially larger percentage of progeny as an unattached 
fraction available to be deposited in the lung; maintaining a consistent 
air volume setting; human interference with filtration device operation; 
uncertainties  with  filter  loading  and  progeny  reductions;  and the 
frequency  of  radon  progeny measurements needed to maintain the target 
progeny concentration.

Technical assistance.   Further technical assistance may be available to 
assist  you  in your ZCES deliberations.  Radon professionals at EPA and 
the  State  of  Nevada are available to support you through letters like 
this,  via conference calls, etc.  Also, onsite technical assistance may 
be  available  through  the  Conference  of  Radiation  Control  Program 
Directors  (CRCPD).   For  such a request you should contact Adrian Howe 
with the Nevada State Radon Program (775-687-7531, ahowe@health.nv.gov).

We  acknowledge  the  good  offices  of  the State of Nevada Radon 
Program in addressing this issue to date.  Thank you for the opportunity 
of joining in the effort to assist the Douglas County School District in 
resolving this important public health issue.

Sincerely,

Phil Jalbert [signed]                           Gene Fisher [signed] 
Radon Team Leader                         Health Physicist 
202-343-9431                                    202-343-9418 
jalbert.philip@epa.gov                          fisher.eugene@epa.gov

cc: 
Ms.  Holly  Luna,  Director,  Business  Services,  Douglas County School 
District 
Ms. Carol Lark, Superintendent, Douglas County School District 
Dr.   Susan   Conrath,   MPH,  PhD,  U.S.  Public  Health  Service,  EPA 
Mr. Bill Long, Director, EPA Center for Radon and Air Toxics, EPA 
Mr. Adrian Howe, State of Nevada Radon Program 
Ms. Louise Hill, EPA Region 9 Radon Coordinator 
Ms. Kelly Krolicki 
Mr. Greg Felton

----------------- 
Philip P. Jalbert 
202.343.9431 
Radon/SIRG Team Leader 
www.epa.gov/radon

Executive Secretary, Federal Interagency Committee on Indoor Air Quality 
(CIAQ) 
www.epa.gov/iaq/ciaq/index.html 
Subscribe to the CIAQ Listserve! for meeting notices/minutes, etc. 
Send an email w/a blank 'subject' line to  ciaq-subscribe@lists.epa.gov

Indoor Environments Division (IED)(6609-J) 
U.S. Environmental Protection Agency 
1200 Pennsylvania Avenue, N.W., Washington, DC 20460-0001

[DELIVERY Address] 
Room 431 
1310 L Street, N.W., Washington, DC 20005-4113